## Slide 1
TEMA X. TURBINAS DE HIDRÓGENO
TURBINAS DE HIDRÓGENO EXISTENTES EN EL MERCADO
Tema V Turbina de hidrógeno

## Slide 2: AGENDA
INTRODUCTION.
ADVANTAGES OF HYDROGEN GAS TURBINES
HYDROGEN COMBUSTION
RETROFIT OF EXISTING GAS TURBINES
CURRENT CAPABILITIES OF GAS TURBINES BURNING HYDROGEN
Tema V Turbina de hidrógeno

## Slide 3: AGENDA
INTRODUCTION.
ADVANTAGES OF HYDROGEN GAS TURBINES
HYDROGEN COMBUSTION
RETROFIT OF EXISTING GAS TURBINES
CURRENT CAPABILITIES OF GAS TURBINES BURNING HYDROGEN
Tema V Turbina de hidrógeno

## Slide 4: Introduction
Gas Turbines (GT) use natural or synthetic gas to provide dispatchable power and heat following the system and market requirements. In a system with an increasing share of variable electricity production from non-dispatchable renewable energy sources, the high flexibility of gas turbine-based power plants can effectively ensure the grid stability and security of supply. Used also in cogeneration systems, they can flexibly provide the necessary amounts of power and heat for industrial settings or district heating.
Their main advantage lies in the power density, which enables large amounts of power being available within a very short time and with a small footprint. Moreover, GT have a significant fuel flexibility, being able to burn a large variety of different fuel and with varying fuel composition.
GTs can reach thermal efficiencies up to ~43% as Open Cycle Gas Turbine (OCGT) and up to ~63% in Combined Cycle Gas Turbine (CCGT) configurations. In cogeneration mode, the fuel conversion rate reached is above 90%.
Tema V Turbina de hidrógeno

## Slide 5: Introduction
With the increasing admixture of decarbonised and renewable gases in the gas network, such as hydrogen, gas turbines increasingly become a source of sustainable dispatchable power and heat that deliver at any time according to the system needs. This in turn allows for additional amounts of variable renewables to be integrated into the system, supporting therefore Europe’s energy system decarbonisation pathway. A fuel switch to hydrogen aims to retain all present strengths of gas turbines while ensuring carbon-free energy conversion.
Yet, the use of diluents or Wel Low Emmision combustion (legacy technology) provides today only a sub-optimal solution to hydrogen firing of GTs and the aim of future R&D is to achieve 100% H2 firing by Dry Low Emmisions combustion, still complying with NOx emissions targets (< 25 ppm) without the use of diluents and with minimal thermal efficiency penalty.
Gas turbine technologies provide a unique opportunity to reutilise existing infrastructure, reducing investment costs in new infrastructure and ensuring a cost-competitive transition to renewable gases and zero-carbon power generation. They do not pose strict requirements to fuel gas purity and are able to handle unproblematically
Tema V Turbina de hidrógeno

## Slide 6: AGENDA
INTRODUCTION.
ADVANTAGES OF HYDROGEN GAS TURBINES
HYDROGEN COMBUSTION
RETROFIT OF EXISTING GAS TURBINES
CURRENT CAPABILITIES OF GAS TURBINES BURNING HYDROGEN
Tema V Turbina de hidrógeno

## Slide 7: ADVANTAGES OF HYDROGEN GAS TURBINES
Tema V Turbina de hidrógeno
In January 2019, the gas turbine industry strongly committed to develop gas turbines operating with 100% hydrogen till 2030, such fully supporting the transformation of the European gas grid into a renewable-based energy system by overcoming technical challenges and ensuring that this transformation takes place swiftly.
Gas turbines already fulfil the crucial balancing role in the energy system. By extending the fuel capabilities of gas turbines to hydrogen, their role can become predominant in the energy transition in long-term energy strategies:
In combined cycle configuration (CCGT), gas turbines are already the cleanest form of thermal power generation.
Mixing renewable gas (e.g. green hydrogen, biogas, syngas) with natural gas enables further reduction in net CO2 emissions.
Industry is committed to enable gas turbines to run entirely on renewable gas fuels by 2030 and therefore achieve capabilities for 100% carbon neutral gas fired power generation.
Gas turbines are flexible, well-suited for frequent starts, and able to provide a fast response to grid demands, making them complementary to the variable RES.

## Slide 8: ADVANTAGES OF HYDROGEN GAS TURBINES
Tema V Turbina de hidrógeno

## Slide 9: ADVANTAGES OF HYDROGEN GAS TURBINES
Tema V Turbina de hidrógeno
Hydrogen gas turbines would, in essence, complement the intermittent nature of wind and solar power since they can be used as back-up power. Hydrogen can be
produced via electrolysis, using excess renewable power during periods of abundant wind and daylight, or by natural gas reformation, which is also carbon neutral resource if carbon capture technology is utilised.
In this context hydrogen reforming can be seen as the kick-starter to create sufficient hydrogen supply on short notice and enable the creation of a hydrogen infrastructure, including storages. The scalability of gas turbines from small decentralised to large centralized systems allows for adaptation to the production capability and local storage. All in all, hydrogen gas turbines can be an enabler for long term energy storage with power to gas technologies.
The development of retrofit solutions for existing gas turbines will be a key enabler for the implementation of the hydrogen gas turbine technology. The first steps can initially be achieved with relatively small modifications to existing combustors, allowing co-firing of hydrogen to significant fractions (>30 % vol., 11% of carbon reduction).

## Slide 10: ADVANTAGES OF HYDROGEN GAS TURBINES
Tema V Turbina de hidrógeno
Increased field experience will enable further developments, such as new types of combustors allowing up to 100% of hydrogen firing without the need for diluents for emission control.
Due to the non-linear dependency of carbon content in the fuel versus the volumetric hydrogen content, it is of importance to enable the use of higher hydrogen content as soon as possible to maximize the impact on CO2 emissions.

## Slide 11: ADVANTAGES OF HYDROGEN GAS TURBINES
Tema V Turbina de hidrógeno
UTILISING THE EXISTING NATURAL GAS INFRASTRUCTURE
Gas turbines use the robust and flexible natural gas infrastructure to source their fuel. With little to no modifications a blend of hydrogen with natural gas can be transported within this existing infrastructure, which makes the entire system reusable without major expenditure.
For example the Netherlands has already injected up to 20% hydrogen into their natural gas grid in a pilot project on the Island of Ameland some years ago 3. This concept can be replicated to other regions to start burning a blend of natural gas and hydrogen in gas turbines to reduce carbon emissions. However, new or retrofitted piping infrastructure would be necessary for 100% hydrogen transport, but combusting hydrogen at the point of production would be a solution to this problem during the initial phase.

## Slide 12: ADVANTAGES OF HYDROGEN GAS TURBINES
Tema V Turbina de hidrógeno
RETROFITTING EXISTING GAS TURBINES
The design of hydrogen gas turbines can rely to some extent on the existing gas turbine technology. There is no necessity to design and manufacture entirely new gas turbines for hydrogen combustion. Special attention is required on modifying the combustor and some auxiliary parts, but most of existing gas turbines can be retrofitted to either partially or fully burn hydrogen. This conversion would not only avoid large capital spending but also save time in switching large fleets of current gas turbines to hydrogen. An additional major benefit of developing and deploying the hydrogen gas turbine

## Slide 13: ADVANTAGES OF HYDROGEN GAS TURBINES
Tema V Turbina de hidrógeno
100% EMISSION COMPLIANCE
Current gas turbines can already burn pure hydrogen via diffusion combustion, thus still generating NOx emissions.
For this reason research and development activities are nowadays focused on dry low NOx technology, which has the potential to substantially reduce or eliminate NOx emissions.
In terms of thermal efficiency and power output, differences between current gas turbines and hydrogen turbines, both with dry low NOx technology, would be marginal.

## Slide 14: ADVANTAGES OF HYDROGEN GAS TURBINES
Tema V Turbina de hidrógeno
SECTOR COUPLING FOR DEEPER DECARBONISATION
The heating sector is one of the largest carbon emitters worldwide. In order to reduce the CO2 emissions, waste heat from hydrogen gas turbines in Combined Heat and Power (CHP) plants can be used.
By coupling hydrogen gas turbines also with other industries (e.g. chemicals and refineries), further decarbonisation can be achieved.

## Slide 15: ADVANTAGES OF HYDROGEN GAS TURBINES
Tema V Turbina de hidrógeno
WIDER HYDROGEN DEPLOYMENT
Given its peculiarities, hydrogen gas turbines can stimulate commercial demand for large amount of low purity hydrogen, thus contributing to the reduction of hydrogen’s production costs and to its wider deployment in multiple sectors.
Further costs reduction across the whole hydrogen value chain can be achieved through R&D.
In this regard, governmental funding schemes for gas turbine R&D worldwide can be key contributors towards a hydrogen society.
Collaboration between internal actors is needed to address to eliminate the barriers for the wider deployment of hydrogen-based solutions.

## Slide 16: AGENDA
INTRODUCTION.
ADVANTAGES OF HYDROGEN GAS TURBINES
HYDROGEN COMBUSTION
RETROFIT OF EXISTING GAS TURBINES
CURRENT CAPABILITIES OF GAS TURBINES BURNING HYDROGEN
Tema V Turbina de hidrógeno

## Slide 17: HYDROGEN COMBUSTION
Tema V Turbina de hidrógeno
In the transition to a hydrogen based energy system, fuel flexible gas turbines are needed to utilise blends of hydrogen and other gaseous fuels, such as natural gas.
Combustors need to cope with a wide range of natural gas/H2-mixtures as well as with fast changes in the fuel composition.
In the medium-term, fuel-flexible gas turbines capable of burning hydrogen/natural gas blends containing higher amounts of H2 than nowadays need to be developed.
In the long-term, gas turbines offering the full fuel flexibility (any blend of hydrogen and natural gas as well as pure hydrogen) need to be developed, which requires intensive R&D activity in order to pave the way for such a technology.

## Slide 18: HYDROGEN COMBUSTION
Tema V Turbina de hidrógeno
The Dry Low Emission (DLE) technology has the potential to enable fuel flexible operation at 0-100% H2 with low emissions. However, further development effort is required to derive technical solutions with respect to the following challenges associated with high hydrogen contents in the fuel:
Autoignition: High reactivity of hydrogen inherently increases the auto-ignition risk in the premixing section which needs to be addressed in future combustor developments. This might be of a particular challenge in some systems with very high air inlet temperatures, e.g. in modern high-efficient gas turbines or micro gas turbines due to the recuperator.
Flashback: Burning hydrogen-rich fuels inherently increases flashback risks because of a higher flame speed or a shorter ignition delay time compared to natural gas. This may be a particular challenge in some systems with very high air inlet temperatures.
Modified thermo-acoustic amplitude level and frequencies: Compared to natural gas flames, hydrogen flames exhibit significantly different thermoacoustic behaviour. This is due to higher flame speed, shorter ignition delay time and distinct flame stabilization mechanisms resulting in different flame shapes, positions and different reactivity.

## Slide 19: HYDROGEN COMBUSTION
Tema V Turbina de hidrógeno
Higher flame temperature, NOx emissions: The higher adiabatic flame temperature of H2 will result in higher NOx emissions if no additional measures are undertaken. Some flexibility might be needed on NOx limits in future, in order to enable the decarbonisation. It will be particularly a challenge to achieve even stricter NOx-limits foreseen in the future.
Reduced lifetime /improved cooling of hot gas path components: Burning hydrogen instead of natural gas will increase the moisture content in the exhaust gas causing higher heat transfer to the gas turbine hot gas path components. This will require an adaptation of the cooling in order to avoid overheating of components. In addition, due to the higher moisture content hot corrosion is more likely to occur. Therefore, measures need to be undertaken to avoid these effects.
Wobbe Index change: Compared to burning natural gas at the same thermal power, a larger volumetric fuel flow rate is needed when burning hydrogen due to its lower volumetric Lower Heating Value (LHV). In addition, hydrogen has a lower Wobbe Index (WI) which is the most commonly used parameter for specifying the acceptability of a gaseous fuel in a combustion system. Thus the greater the change in Wobbe Index, the greater the required flexibility of the combustion systems and associated control.

## Slide 20: HYDROGEN COMBUSTION
Tema V Turbina de hidrógeno

## Slide 21: AGENDA
INTRODUCTION.
ADVANTAGES OF HYDROGEN GAS TURBINES
HYDROGEN COMBUSTION
RETROFIT OF EXISTING GAS TURBINES
CURRENT CAPABILITIES OF GAS TURBINES BURNING HYDROGEN
Tema V Turbina de hidrógeno

## Slide 22: RETROFIT OF EXISTING GT
Tema V Turbina de hidrógeno
Every machine has to be evaluated on a case by case basis for hydrogen consumption, considering fuel skid, controls, and combustion system. As a general guideline, there are break points to consider, namely:
Low levels of hydrogen mixed with natural gas, to a level that does not require any changes to materials, designs and control and protection. These levels may be considered to be in the range of [0-10% vol.], depending on system.
Medium levels of hydrogen mixed with natural gas, to a level that does not require significant changes to materials, designs, control and protection. These levels may be considered to be in the range of [10- 30% vol.]
Higher levels of hydrogen, which require a wider retrofit scope, and which probably then economically suggest that hydrogen fuel capability should be maximized given the assumption of fuel delivery, combustion module, control and protection retrofit [30-100% vol.]

## Slide 23: RETROFIT OF EXISTING GT
Tema V Turbina de hidrógeno
GENERAL FUEL PREPARATION CONSIDERATIONS
When using hydrogen as fuel, it is of utmost importance to take into consideration the delivery pressure and temperature in order to avoid embrittlement in the pipelines and other auxiliaries.
Existing piping and gas turbine valves shall be subject to retrofit when a gas turbine manifold running with natural gas is forecasted to run with H2. Changes may include new valves design with a different sealing arrangement, and potentially new piping material.
While hydrogen embrittlement does not occur in stainless steel equipment at 50 barg and 100°C, increasing the temperature to around 200°C may cause H2 migration through the material. Indeed H2 embrittlement is a concern at temperatures above 200°C, although 316L grade stainless steel is considered quite suitable in reducing this effect. It is worth noting that, hydrogen embrittlement is not only related to temperature, but also to the stress endured by the material which affects the permeation of H2.

## Slide 24: RETROFIT OF EXISTING GT
Tema V Turbina de hidrógeno
FUEL FLEXIBILITY
The rate of change of fuel mix (natural gas/hydrogen) will be a key requirement to be met by future power plants which, in the foreseeable future, will mostly consist of retrofit units from the existing installed asset base. A natural gas-dominant or liquid fuel start-up fuel feed is often the basis on which these units will be safely managed on start-up and maybe also on shut-down. The preferred alternative would be to use the same fuel for startup and normal operations.
The operators of these assets will look for gas turbine solutions that do not constrain fuel delivery (i.e. that match the variation in hydrogen concentration in the fuel pipeline) due to variations in hydrogen production.
For gas turbines connected to the gas transmission network, it is not possible to control the composition of fuel delivered to the plant. While the proportion of hydrogen introduced into the networks may increase gradually over time, it is anticipated that regional initiatives will cause the hydrogen content to increase much more rapidly in some locations.

## Slide 25: RETROFIT OF EXISTING GT
Tema V Turbina de hidrógeno
IMPACT ON HOT GAS PATH PARTS LIFETIME
It is likely that hot gas path temperature profiles will be altered with the retrofit to a hydrogen-flexible combustion system. Whilst it is possible that temperature variations will decrease with micro-injector style (multi-point) fuel injectors, it is also almost inevitable that original hot gas path components will see temperature profiles that are different to those that they were originally designed for. The variations will be more or less significant on each engine type, and therefore cannot be generalised.
It is correct to assume that each retrofit solution should be qualified as a mini-New-Product-Introduction, with appropriate qualification and risk management of key engine hot gas path components. A mix of validation by similarity, increased inspection, and analysis of ex-service components will be part of this qualification process.
If a diluent (water or steam) is required for NOx control, this will typically reduce the maintenance interval for the hot gas path components or lead to gas turbine derating.

## Slide 26: RETROFIT OF EXISTING GT
Tema V Turbina de hidrógeno
REQUIREMENTS FOR RETROFIT PACKAGES
Most customers for asset retrofits will be large utilities, refineries or large process customers. Their project requirements will include risk mitigation and qualification of new product as part of the requirements for any project. This implies that any hydrogen fuel retrofit will be either the purchase of a highly qualified and defined option or module for a mainstream gas turbine model or it will be a pilot programme purchase of such a product. This work is unlikely to be carried out as a single engine modification, due to the high product development investment cost.
A retrofit package is likely to include:
Core gas turbine combustion module replacement
Instrumentation and fuel control system modification
Plant fuel delivery system modification, including modified purge, metering, gas composition monitoring, safety systems (including package sensing and ventilation upgrades) and the provision of a start-up fuel supply.
It is likely that the economics of such a retrofit assume re-use of existing hot gas path designs of components.

## Slide 27: AGENDA
INTRODUCTION.
ADVANTAGES OF HYDROGEN GAS TURBINES
HYDROGEN COMBUSTION
RETROFIT OF EXISTING GAS TURBINES
CURRENT CAPABILITIES OF GAS TURBINES BURNING HYDROGEN
Tema V Turbina de hidrógeno

## Slide 28: CURERNT CAPABILITIES
Tema V Turbina de hidrógeno

## Slide 29: CURERNT CAPABILITIES
Tema V Turbina de hidrógeno
GE has been providing gas turbines for operation on fuels with hydrogen for over 30 years. More than 75 GE gas turbines have operated on fuels containing hydrogen, accumulating more than 5 million operating hours. These units have operated on fuels with a range of hydrogen content, from 5% (by volume) up to 100%. This experience includes both heavy-duty and aeroderivative gas turbines in a range of applications.

## Slide 30: CURERNT CAPABILITIES
Tema V Turbina de hidrógeno
The primary fuel for all MAN Energy Solution gas turbines is natural gas, while liquid fuel and dual fuel capability is offered as an option. Fuel flexibility has been a design requirement from the beginning.
The gas turbines are available with a standard diffusion combustion system. This system allows up to 60% vol. H2 content in a mixture with natural gas, but requires exhaust gas treatment when low NOx emissions are a requirement.
Some models are also offered with a dry low emission combustion system. These systems achieve very low emissions without water injection or exhaust treatment, and can also handle up to 20% vol. hydrogen.
With some additional modifications, stable and low emission combustion was achieved even up to 50% vol. hydrogen.

## Slide 31: CURERNT CAPABILITIES
Tema V Turbina de hidrógeno
Mitsubishi Hitachi Power Systems (MHPS) has developed 3 types of combustors for hydrogen-fired gas turbines that can be used for the cofiring and firing of hydrogen.
Multi-nozzle combustor. 30% vol. H2 mix in natural.
Multi-cluster combustor. Combustion characteristics with 80% vol. H2 cofiring have been confirmed at rig test.
Diffusion combustor. Uses fuel with up to 90% vol. H2 content and has been in operation for more than 3 million hours with diffusion combustors.

## Slide 32: CURERNT CAPABILITIES
Tema V Turbina de hidrógeno

## Slide 33: CURERNT CAPABILITIES
Tema V Turbina de hidrógeno
Solar Turbines has gathered experience with many applications operating with significant concentrations of hydrogen. In the past decade many of these have been using Coke Oven Gas (COG) on Titan 130 and Taurus 60 generator sets.
COG is a typically waste gas generated in the process of creating coke for steel production. The typical gas turbine fuel created with COG has 55 to 60% vol. hydrogen, 25 to 30% vol. methane, 5 to 10% vol. CO, and 5 to 10% vol. diluents (N2+CO2).

## Slide 34: ¡¡MUCHAS GRACIAS POR SU ATENCIÓN!!
ÍNDICE
Tema V TURBINAS DE HIDRÓGENO